## _fandata
DIMENSIONS - FANS WITH FEET
DIMENSIONS - FANS WITH FRAMES
|  | 35 | 35
|  | 40 | 60
Definition of Data Fields / Dimensions
Field Name | Definition
ID | Record ID - for internal database use. Must be unique.
FAN_MANUF | Fan manufacturer. E.g. Nicotra, Gebhardt
FAN_REF | Fan Range Reference. E.g. ADH, ASH, RZR, TZR
TYPE | Fan inlet/impeller type. May be DIDW or SISW.
IMPELLER | Number of impellers on fan. SINGLE for 1 impeller, DUPLEX for 2 impellers.
MOUNT | Fan mounting type. FEET for movable feet or FRAMES for side frames.
DB_MOUNT | Mounting type when fan is in downblast position. May be FEET or FRAMES as above or may be FLANGE if fan is bolted down using outlet flange.
FAN_CODE | Fan reference code as used by AHU manufacturer.
FAN_DIAM | Nominal impeller diameter in mm.
A | Height of fan scroll parallel to outlet, excluding feet & outlet flanges OR Height of side frame in same plane
B | Length of fan scroll perpendicular to outlet, excluding outlet flange OR Length of side frame in same plane
D | Centres (parallel to shaft) of foot/frame fixing holes.
F | Total length of fan shaft (DIDW & DUPLEX) OR total width of fan incl shaft (SISW)
FT | Flange thickness. May be 0 if outlet flanges are not used.
H1 | Height from bottom of feet/frame to shaft centre in horizontal high pos.
H2 | Height from bottom of feet/frame to shaft centre in horizontal low pos.
H3 | Height from bottom of feet/frame to shaft centre in upblast pos.
H4 | Height from bottom of feet/frame to shaft centre in downblast pos. May be height from outlet flange to shaft centre if fan mounted on flange.
J1 | Distance from fan outlet to 1st fixing hole in horizontal high pos.
J2 | Distance from fan outlet to 1st fixing hole in horizontal low pos.
J3 | Distance from fan outlet to 1st fixing hole in upblast pos.
J4 | Distance from fan outlet to 1st fixing hole in downblast pos.
K1 | Centres (perpendicular to shaft) of foot/frame fixing holes in horizontal pos.
K2 | Centres (perpendicular to shaft) of foot/frame fixing holes in upblast pos.
K3 | Centres (perpendicular to shaft) of foot/frame fixing holes in downblast pos.
L | Depth of outlet overhang from scroll body OR from side frames.
M | Distance from shaft centre to bottom/back of scroll, parallel to outlet.
N | Distance from shaft centre to top of fan outlet.
OH | Outlet Height
OW | Outlet width
P | Distance from shaft centre to bottom/back of scroll, perpendicular to outlet.
Q | Distance from shaft centre to outlet.
S | Shaft diameter.
T | Fixing hole diameter.
U | Width, parallel to shaft, across mounting feet or side frames.
V | DUPLEX only - gap between duplex fan outlets
W | DUPLEX only - gap between 2 sets of fixing holes.
Weight | Weight of fan.

## FANDATA
ID | FAN_REF | TYPE | MOUNT | FAN_CODE | FAN_SIZE | FAN_DIAM | A | B | D | F | FT | H1 | H2 | H3 | H4 | J1 | J2 | J3 | J4 | K1 | K2 | K3 | L | M | N | OH | OW | P | Q | S | T | U | V | W | Critical_Height
1 | FDA / BDB / ADH / RDH | DIDW | FRAMES | FDA180CM | 180 | 180 | 336 | 294 | 248 | 392 | 0 | 144 | 192 | 171 | 152 | 86 | 86 | 78 | 78 | 180 | 180 | 180 | 29 | 139 | 197 | 228 | 228 | 171 | 152 | 20 | 9 | 268 | 180 | 180 | 40
2 | FDA / BDB / ADH / RDH | DIDW | FRAMES | FDA200CM | 200 | 200 | 370 | 306 | 281 | 420 | 0 | 155 | 215 | 179 | 164 | 78 | 78 | 73 | 73 | 224 | 224 | 224 | 37 | 151 | 219 | 256 | 256 | 179 | 164 | 20 | 11 | 306 | 200 | 200 | 40
3 | FDA / BDB / ADH / RDH | DIDW | FRAMES | FDA225CM | 225 | 225 | 415 | 348 | 313 | 452 | 0 | 172 | 243 | 202 | 180 | 96 | 96 | 95.5 | 95.5 | 224 | 224 | 224 | 34 | 169 | 246 | 288 | 288 | 202 | 180 | 20 | 11 | 338 | 225 | 225 | 40
4 | FDA / BDB / ADH / RDH | DIDW | FRAMES | FDA250CM | 250 | 250 | 460 | 383 | 347 | 486 | 0 | 190 | 270 | 224 | 194 | 114.5 | 114.5 | 118 | 118 | 224 | 224 | 224 | 35 | 186 | 274 | 322 | 322 | 224 | 194 | 20 | 11 | 372 | 250 | 250 | 40
5 | FDA / BDB / ADH / RDH | DIDW | FRAMES | FDA280CM | 280 | 280 | 518 | 432 | 390 | 556 | 0 | 216 | 302 | 252 | 214 | 110 | 110 | 119 | 119 | 280 | 280 | 280 | 34 | 211 | 307 | 360 | 360 | 252 | 214 | 25 | 13 | 420 | 280 | 280 | 40
6 | FDA / BDB / ADH / RDH | DIDW | FRAMES | FDA315CM | 315 | 315 | 578 | 480 | 434 | 600 | 0 | 238 | 340 | 282 | 236 | 113 | 113 | 124 | 124 | 330 | 330 | 330 | 38 | 235 | 343 | 404 | 404 | 282 | 236 | 25 | 13 | 464 | 315 | 315 | 40
7 | FDA / BDB / ADH / RDH | DIDW | FRAMES | FDA355CM | 355 | 355 | 654 | 548 | 492 | 672 | 0 | 271 | 383 | 318 | 260 | 120 | 120 | 143 | 143 | 368 | 368 | 368 | 30 | 265 | 389 | 452 | 452 | 318 | 260 | 30 | 13 | 532 | 355 | 355 | 40
8 | FDA / BDB / ADH / RDH | DIDW | FRAMES | FDA400CM | 400 | 400 | 736 | 612 | 546 | 726 | 0 | 304 | 432 | 360 | 290 | 143 | 143 | 167 | 167 | 402 | 402 | 402 | 38 | 299 | 437 | 506 | 506 | 360 | 290 | 30 | 13 | 586 | 400 | 400 | 40
9 | FDA / BDB / ADH / RDH | DIDW | FRAMES | FDA450CM | 450 | 450 | 827 | 681 | 608 | 814 | 0 | 341 | 491 | 404 | 322 | 130 | 130 | 158 | 158 | 511 | 511 | 511 | 45 | 336 | 491 | 568 | 568 | 404 | 322 | 35 | 13 | 648 | 450 | 450 | 60
10 | FDA / BDB / ADH / RDH | DIDW | FRAMES | FDA500CM | 500 | 500 | 918 | 750 | 678 | 924 | 0 | 380 | 538 | 448 | 352 | 120 | 120 | 154 | 154 | 610 | 245 | 245 | 50 | 375 | 543 | 638 | 638 | 448 | 352 | 35 | 13 | 718 | 500 | 500 | 60
11 | FDA / BDB / ADH / RDH | DIDW | FRAMES | FDA560CM | 560 | 560 | 1030 | 844 | 764 | 1000 | 0 | 427 | 603 | 502 | 390 | 127.5 | 127.5 | 172.5 | 172.5 | 685 | 280 | 280 | 48 | 420 | 610 | 714 | 714 | 502 | 390 | 40 | 13 | 814 | 560 | 560 | 60
12 | FDA / BDB / ADH / RDH | DIDW | FRAMES | FDA630CM | 630 | 630 | 1157 | 945 | 850 | 1092 | 0 | 478 | 679 | 564 | 434 | 142.5 | 142.5 | 195.5 | 195.5 | 766 | 328 | 328 | 53 | 472 | 685 | 800 | 800 | 564 | 434 | 45 | 13 | 900 | 630 | 630 | 60
13 | FDA / BDB / ADH / RDH | DIDW | FRAMES | FDA710CM | 710 | 710 | 1302 | 1057 | 948 | 1234 | 0 | 537 | 765 | 636 | 484 | 156.5 | 156.5 | 216 | 216 | 870 | 360 | 360 | 63 | 530 | 772 | 898 | 898 | 636 | 484 | 50 | 17 | 998 | 710 | 710 | 0
14 | FDA / BDB / ADH / RDH | DIDW | FRAMES | FDA800TM | 800 | 800 | 1468 | 1180 | 1056 | 1388 | 0 | 599 | 869 | 714 | 540 | 173.5 | 173.5 | 243.5 | 243.5 | 981 | 981 | 981 | 74 | 599 | 869 | 1006 | 1006 | 714 | 540 | 55 | 17 | 1106 | 800 | 800 | 0
15 | FDA / BDB / ADH / RDH | DIDW | FRAMES | FDA900TM | 900 | 900 | 1648 | 1319 | 1180 | 1566 | 0 | 670 | 978 | 804 | 604 | 199 | 199 | 274.5 | 274.5 | 1099 | 1099 | 1099 | 89 | 670 | 978 | 1130 | 1130 | 804 | 604 | 60 | 17 | 1230 | 900 | 900 | 0
16 | FDA / BDB / ADH / RDH | DIDW | FRAMES | FDA1000TM | 1000 | 1000 | 1810 | 1450 | 1316 | 1724 | 0 | 735 | 1075 | 884 | 656 | 215 | 215 | 305 | 305 | 1200 | 1200 | 1200 | 90 | 735 | 1075 | 1266 | 1266 | 884 | 656 | 70 | 17 | 1366 | 1000 | 1000 | 0
17 | FDA / BDB / ADH / RDH | DIDW | FRAMES | FDA1120TM | 1120 | 1120 | 2033 | 1630 | 1483 | 1800 | 0 | 824 | 1209 | 977 | 748 | 385 | 385 | 290 | 290 | 1145 | 1145 | 1145 | 95 | 824 | 1209 | 1422 | 1422 | 977 | 748 | 75 | 17 | 1548 | 1120 | 1120 | 0
18 | FDA / BDB / ADH / RDH | DIDW | FRAMES | FDA1250TM | 1250 | 1250 | 2285 | 1831 | 1599 | 1975 | 0 | 923 | 1362 | 1100 | 830 | 399 | 399 | 300 | 300 | 1330 | 1330 | 1330 | 99 | 923 | 1362 | 1524 | 1524 | 1100 | 830 | 80 | 17 | 1674 | 1250 | 1250 | 0
19 | FDA / BDB / ADH / RDH | DIDW | FRAMES | FDA1400TM | 1400 | 1400 | 2568 | 2057 | 1869 | 2260 | 0 | 1040 | 1528 | 1207 | 963 | 423 | 423 | 310 | 310 | 1550 | 1550 | 1550 | 113 | 1040 | 1528 | 1794 | 1794 | 1207 | 963 | 90 | 17 | 1869 | 1400 | 1400 | 0
20 | KAT / AT | DIDW | FEET | KAT7/7SL | 7 / 7 | 7 / 7 | 328 | 312 | 279 | 355 | 0 | 164 | 224 | 164 | 152 | 66 | 66 | 66 | 66 | 180 | 180 | 180 | 0 | 136 | 192 | 228 | 259 | 160 | 152 | 20 | 11 | 299 | 0 | 0 | 40
21 | KAT / AT | DIDW | FEET | KAT8/8SL | 8 / 8 | 8 / 8 | 364 | 345 | 312 | 392 | 0 | 181 | 245 | 184 | 164 | 60.5 | 60.5 | 60.5 | 60.5 | 224 | 224 | 224 | 0 | 148 | 216 | 256 | 287 | 181 | 164 | 20 | 11 | 337 | 0 | 0 | 40
22 | KAT / AT | DIDW | FEET | KAT9/7SL | 9 / 7 | 9 / 7 | 387 | 380 | 257 | 321 | 0 | 178 | 233 | 199 | 185 | 40 | 40 | 40 | 40 | 300 | 300 | 300 | 0 | 171 | 216 | 262 | 232 | 195 | 185 | 20 | 11 | 282 | 0 | 0 | 40
23 | KAT / AT | DIDW | FEET | KAT9/9SL | 9 / 9 | 9 / 9 | 387 | 380 | 323 | 392 | 0 | 178 | 233 | 199 | 185 | 40 | 40 | 40 | 40 | 300 | 300 | 300 | 0 | 171 | 216 | 262 | 298 | 195 | 185 | 20 | 11 | 348 | 0 | 0 | 40
24 | KAT / AT | DIDW | FEET | KAT10/8SL | 10 / 8 | 10 / 8 | 443 | 425 | 290 | 355 | 0 | 198 | 287 | 227 | 203 | 42.5 | 42.5 | 42.5 | 42.5 | 340 | 340 | 340 | 0 | 194 | 249 | 289 | 265 | 222 | 203 | 20 | 11 | 315 | 0 | 0 | 40
25 | KAT / AT | DIDW | FEET | KAT10/10SL | 10 / 10 | 10 / 10 | 443 | 425 | 356 | 425 | 0 | 198 | 287 | 227 | 203 | 42.5 | 42.5 | 42.5 | 42.5 | 340 | 340 | 340 | 0 | 194 | 249 | 289 | 331 | 222 | 203 | 20 | 11 | 381 | 0 | 0 | 40
26 | KAT / AT | DIDW | FEET | KAT12/9SL | 12 / 9 | 12 / 9 | 521 | 491 | 334 | 420 | 0 | 232 | 332 | 266 | 230 | 41.5 | 41.5 | 41.5 | 41.5 | 408 | 408 | 408 | 0 | 227 | 294 | 341 | 309 | 261 | 230 | 25 | 11 | 359 | 0 | 0 | 40
27 | KAT / AT | DIDW | FEET | KAT12/12SL | 12 / 12 | 12 / 12 | 521 | 491 | 420 | 510 | 0 | 232 | 332 | 266 | 230 | 41.5 | 41.5 | 41.5 | 41.5 | 408 | 408 | 408 | 0 | 227 | 294 | 341 | 395 | 261 | 230 | 25 | 11 | 445 | 0 | 0 | 40
28 | KAT / AT | DIDW | FEET | KAT15/11SL | 15 / 11 | 15 / 11 | 609 | 569 | 398 | 510 | 0 | 272 | 380 | 309 | 264 | 37 | 37 | 37 | 37 | 495 | 495 | 495 | 0 | 267 | 342 | 404 | 373 | 305 | 264 | 25 | 11 | 423 | 0 | 0 | 40
29 | KAT / AT | DIDW | FEET | KAT15/15SL | 15 / 15 | 15 / 15 | 609 | 569 | 496 | 608 | 0 | 272 | 380 | 309 | 264 | 37 | 37 | 37 | 37 | 495 | 495 | 495 | 0 | 267 | 342 | 404 | 471 | 305 | 264 | 25 | 11 | 521 | 0 | 0 | 40
30 | KAT / AT | DIDW | FEET | KAT18/13SL | 18 / 13 | 18 / 13 | 739 | 684 | 455 | 567 | 0 | 340 | 457 | 376 | 314 | 39 | 39 | 39 | 39 | 606 | 606 | 606 | 0 | 324 | 415 | 478 | 430 | 370 | 314 | 25 | 11 | 480 | 0 | 0 | 40
31 | KAT / AT | DIDW | FEET | KAT18/18SL | 18 / 18 | 18 / 18 | 739 | 684 | 582 | 694 | 0 | 340 | 457 | 376 | 314 | 39 | 39 | 39 | 39 | 606 | 606 | 606 | 0 | 324 | 415 | 478 | 557 | 370 | 314 | 25 | 11 | 607 | 0 | 0 | 40

## MBDIMS
SNO | MB_MODEL | MB_LEN | MB_WT | MB_HT | MOT_MINSIZE | MOT_MAXSIZE | CLEARANCE
1 | 63-100 | 270 | 178 | 31 | 63 | 90 | 25
2 | 112-132 | 380 | 232 | 31 | 100 | 132 | 25
3 | 160-160 | 450 | 338 | 35 | 160 | 180 | 25
4 | 180-200 | 500 | 398 | 35 | 200 | 250 | 25
5 | 225-250 | 550 | 451 | 35 | 250 | 280 | 25

## _mbdims
MOTOR BASE DIMENSIONS
0.66667
Definition of Data Fields / Dimensions
Field Name | Definition
MB_SUPPLIER | Motor base supplier
MB_RANGE | Motor base range - e.g. Quickfit
MB_SIZE | Motor base size - e.g. 63-80
MB_LEN | Motor base length
MB_WT | Motor base width
MB_HT | Motor base height
WEIGHT | Motor base weight
COST | Motor base cost
MOT_MINSIZE | Minimum size motor that will fit on motor base e.g. framesize 63
MOT_MAXSIZE | Maximum size motor that will fit on motor base e.g. framesize 80

## MANUF_DIMS
INDEX | FANSIZE | Back_Motorfan_Gap | SX_Motor_Edge_Clearance | SideMotor_Min_Pulley_Clr | SideMotorFanGapPos1 | SideMotorFanGapPos2
1 | 180 | 50 | 50 | 25 | 50 | 50
2 | 200 | 50 | 50 | 25 | 50 | 50
3 | 225 | 50 | 50 | 25 | 50 | 50
4 | 250 | 50 | 50 | 25 | 50 | 50
5 | 280 | 50 | 50 | 25 | 50 | 50
6 | 315 | 50 | 50 | 25 | 50 | 50
7 | 355 | 50 | 50 | 25 | 50 | 50
8 | 400 | 50 | 50 | 25 | 50 | 50
9 | 450 | 50 | 50 | 25 | 50 | 50
10 | 500 | 50 | 50 | 25 | 50 | 50
11 | 560 | 50 | 50 | 25 | 50 | 50
12 | 630 | 50 | 50 | 50 | 50 | 50
13 | 710 | 50 | 50 | 50 | 50 | 50
14 | 800 | 50 | 50 | 50 | 50 | 50
15 | 900 | 50 | 80 | 50 | 50 | 50
16 | 1000 | 50 | 80 | 50 | 50 | 50
17 | 1120 | 50 | 80 | 50 | 50 | 50
18 | 1250 | 50 | 50 | 25 | 50 | 50
19 | 1400 | 50 | 50 | 25 | 50 | 50
20 | 7 / 7 | 50 | 50 | 25 | 50 | 50
22 | 8 / 8 | 50 | 50 | 25 | 50 | 50
24 | 9 / 7 | 50 | 50 | 25 | 50 | 50
26 | 9 / 9 | 50 | 50 | 25 | 50 | 50
28 | 10 / 8 | 50 | 50 | 25 | 50 | 50
29.2857 | 10 / 10 | 50 | 70 | 25 | 50 | 50
31 | 12 / 9 | 50 | 70 | 25 | 50 | 50
32.7143 | 12 / 12 | 50 | 70 | 25 | 50 | 50
34.4286 | 15 / 11 | 50 | 40 | 25 | 50 | 50
36.1429 | 15 / 15 | 50 | 40 | 25 | 50 | 50
37.8571 | 18 / 13 | 50 | 40 | 25 | 50 | 50
39.5714 | 18 / 18 | 50 | 40 | 25 | 50 | 50

## _manuf_dims
MANUFACTURER SUPPLIED DIMENSIONS
Definition of Data Fields / Dimensions
Field Name | Definition
INDEX | Record ID - for internal database use. Must be unique.
FANSIZE | Nominal diameter of fans to which these dimensions apply
MOT_GAP | Minimum gap from back of fan to start of motor base
SHAFT_OVER | Distance that motor shaft overlaps fan shaft in side-mounted pos.
SHAFT_GAP | Minimum horizontal distance between shaft centres in side-mounted pos.
FLEX_LEN | Length of fan outlet flexible connection
MIN_END_CLR | Minimum clearance from end of fan assembly to end of fan section.
MIN_TOP_CLR | Minimum clearance from top of fan assembly to top of fan section.
BOT_HT | Height of supports underneath AV mounts (May be 0 if not used)
BOT_W | Width of supports underneath AV mounts (May be 0if not used)
MID_HT | Height of 1st layer of frame material above AV mounts
MID_W | Width of 1st layer of frame material above AV mounts
TOP_HT | Height of 2nd layer of frame material above AV mounts
TOP_W | Width of 2nd layer of frame material above AV mounts
MOT_HT | Height of motor support struts (may be 0 if not used)
MOT_W | Width of motor support struts (may be 0 if not used)
MIN_ROOF_GAP | Minimum distance from end of fan section to roof outlet ope
MIN_FLOOR_GAP | Minimum distance from end of fan section to floor outlet ope
MIN_MOT_SPACE | Minimum spacing between 2 motors mounted behind fan
Not used by AHS

## MOTOR_DIMS
FRAMESIZE | AC | E | L1 | D | H | AB | BB | HA | TBW | C | B | A | Motor_Base
FS71 | 136 | 30 | 253 | 14 | 71 | 130 | 110 | 9 | 50 | 45 | 90 | 112 | 63-100
FS80 | 152 | 40 | 290 | 19 | 80 | 147 | 126 | 10 | 50 | 50 | 100 | 125 | 63-100
FS90 | 174 | 50 | 332 | 24 | 90 | 162 | 151 | 13 | 50 | 56 | 100 | 140 | 63-100
FS100 | 200 | 60 | 387 | 28 | 100 | 200 | 180 | 15 | 50 | 63 | 140 | 160 | 63-100
FS112 | 221 | 60 | 392 | 28 | 112 | 230 | 180 | 18 | 50 | 70 | 140 | 190 | 112-132
FS132 | 258 | 80 | 468 | 38 | 132 | 256 | 218 | 20 | 50 | 89 | 140 | 216 | 112-132
FS160 | 305 | 110 | 675 | 42 | 160 | 310 | 310 | 22 | 50 | 108 | 210 | 254 | 160-160
FS180 | 348 | 110 | 705 | 48 | 180 | 324 | 324 | 26 | 50 | 121 | 241 | 279 | 180-200
FS200 | 381 | 110 | 731 | 55 | 200 | 378 | 354 | 30 | 50 | 133 | 267 | 318 | 180-200
FS225 | 442 | 110 | 835 | 60 | 225 | 416 | 360 | 32 | 50 | 149 | 286 | 356 | 225-250
FS250 | 495 | 140 | 910 | 60 | 250 | 473 | 406 | 40 | 50 | 168 | 349 | 406 | 225-250

## _motor_dims
MOTOR DIMENSIONS DATA TABLE
Definition of Data Fields / Dimensions
Field Name | Definition | Units
FRAMESIZE | Motor IEC framesize. Must match the framesize listed in PERF data tables. | None
AC | Outside diameter of motor body. | mm
E | Distance from front of motor body to end of shaft. | mm
L1 | Overall length of motor from end of shaft to back of fan cowl. | mm
D | Shaft diameter. | mm
H | Height from bottom of mounting feet to shaft centre. | mm
AB | Distance from outside of mounting foot to outside of opposite foot. | mm
BB | Overall length of mounting foot. | mm
HA | Mounting foot thickness | mm
TBW | Terminal box width | mm
C | Distance from front of motor casing to centre of first fixing hole. | mm
B | Fixing hole centres parallel to motor shaft. | mm
A | Fixing hole centres perpendicular to motor shaft. | mm

## F_SPA_PUL
GRADE | DIAM | GROOVES | BUSH | CODE
SPA | 80 | 2 | 1108 | SPA 80 x 2
SPA | 85 | 2 | 1108 | SPA 85 x 2
SPA | 90 | 2 | 1108 | SPA 90 x 2
SPA | 95 | 2 | 1610 | SPA 95 x 2
SPA | 100 | 2 | 1610 | SPA 100 x 2
SPA | 106 | 2 | 1610 | SPA 106 x 2
SPA | 112 | 2 | 1610 | SPA 112 x 2
SPA | 118 | 2 | 1610 | SPA 118 x 2
SPA | 125 | 2 | 1610 | SPA 125 x 2
SPA | 132 | 2 | 1610 | SPA 132 x 2
SPA | 140 | 2 | 2012 | SPA 140 x 2
SPA | 150 | 2 | 2012 | SPA 150 x 2
SPA | 160 | 2 | 2012 | SPA 160 x 2
SPA | 180 | 2 | 2012 | SPA 180 x 2
SPA | 200 | 2 | 2517 | SPA 200 x 2
SPA | 250 | 2 | 2517 | SPA 250 x 2
SPA | 315 | 2 | 2517 | SPA 315 x 2
SPA | 400 | 2 | 2517 | SPA 400 x 2
SPA | 500 | 2 | 2517 | SPA 500 x 2
SPA | 630 | 2 | 3020 | SPA 630 x 2
SPA | 80 | 3 | 1108 | SPA 80 x 3
SPA | 85 | 3 | 1108 | SPA 85 x 3
SPA | 90 | 3 | 1610 | SPA 90 x 3
SPA | 95 | 3 | 1610 | SPA 95 x 3
SPA | 100 | 3 | 1610 | SPA 100 x 3
SPA | 106 | 3 | 1610 | SPA 106 x 3
SPA | 112 | 3 | 2012 | SPA 112 x 3
SPA | 118 | 3 | 2012 | SPA 118 x 3
SPA | 125 | 3 | 2012 | SPA 125 x 3
SPA | 132 | 3 | 2012 | SPA 132 x 3
SPA | 140 | 3 | 2517 | SPA 140 x 3
SPA | 150 | 3 | 2517 | SPA 150 x 3
SPA | 160 | 3 | 2517 | SPA 160 x 3
SPA | 180 | 3 | 2517 | SPA 180 x 3
SPA | 200 | 3 | 2517 | SPA 200 x 3
SPA | 250 | 3 | 2517 | SPA 250 x 3
SPA | 315 | 3 | 3020 | SPA 315 x 3
SPA | 400 | 3 | 3020 | SPA 400 x 3
SPA | 500 | 3 | 3020 | SPA 500 x 3
SPA | 630 | 3 | 3020 | SPA 630 x 3

## F_SPB_PUL
GRADE | DIAM | GROOVES | BUSH | CODE
SPB | 125 | 2 | 1610 | SPB 125 x 2
SPB | 132 | 2 | 1610 | SPB 132 x 2
SPB | 140 | 2 | 1610 | SPB 140 x 2
SPB | 150 | 2 | 1610 | SPB 150 x 2
SPB | 160 | 2 | 2012 | SPB 160 x 2
SPB | 170 | 2 | 2012 | SPB 170 x 2
SPB | 180 | 2 | 2012 | SPB 180 x 2
SPB | 190 | 2 | 2517 | SPB 190 x 2
SPB | 200 | 2 | 2517 | SPB 200 x 2
SPB | 212 | 2 | 2517 | SPB 212 x 2
SPB | 224 | 2 | 2517 | SPB 224 x 2
SPB | 236 | 2 | 2517 | SPB 236 x 2
SPB | 250 | 2 | 2517 | SPB 250 x 2
SPB | 280 | 2 | 2517 | SPB 280 x 2
SPB | 315 | 2 | 2517 | SPB 315 x 2
SPB | 355 | 2 | 3020 | SPB 355 x 2
SPB | 400 | 2 | 3020 | SPB 400 x 2
SPB | 500 | 2 | 3020 | SPB 500 x 2
SPB | 630 | 2 | 3030 | SPB 630 x 2
SPB | 125 | 3 | 1610 | SPB 125 x 3
SPB | 132 | 3 | 1610 | SPB 132 x 3
SPB | 140 | 3 | 1610 | SPB 140 x 3
SPB | 150 | 3 | 2012 | SPB 150 x 3
SPB | 160 | 3 | 2517 | SPB 160 x 3
SPB | 170 | 3 | 2517 | SPB 170 x 3
SPB | 180 | 3 | 2517 | SPB 180 x 3
SPB | 190 | 3 | 2517 | SPB 190 x 3
SPB | 200 | 3 | 2517 | SPB 200 x 3
SPB | 212 | 3 | 2517 | SPB 212 x 3
SPB | 224 | 3 | 2517 | SPB 224 x 3
SPB | 236 | 3 | 2517 | SPB 236 x 3
SPB | 250 | 3 | 3020 | SPB 250 x 3
SPB | 280 | 3 | 3020 | SPB 280 x 3
SPB | 315 | 3 | 3020 | SPB 315 x 3
SPB | 355 | 3 | 3020 | SPB 355 x 3
SPB | 400 | 3 | 3525 | SPB 400 x 3
SPB | 500 | 3 | 3525 | SPB 500 x 3
SPB | 630 | 3 | 3525 | SPB 630 x 3

## F_BELTS
ID | Grade | Length | CorrFactor
1 | SPZ | 487 | 0.8
2 | SPZ | 512 | 0.85
3 | SPZ | 562 | 0.85
4 | SPZ | 587 | 0.9
5 | SPZ | 612 | 0.9
6 | SPZ | 630 | 0.95
7 | SPZ | 637 | 0.95
8 | SPZ | 662 | 0.95
9 | SPZ | 670 | 1
10 | SPZ | 687 | 1
11 | SPZ | 710 | 1.05
12 | SPZ | 722 | 1.05
13 | SPZ | 737 | 1.1
14 | SPZ | 750 | 1.1
15 | SPZ | 762 | 1.1
16 | SPZ | 772 | 1.15
17 | SPZ | 787 | 0.8
18 | SPZ | 800 | 0.8
19 | SPZ | 812 | 0.8
20 | SPZ | 825 | 0.8
21 | SPZ | 837 | 0.85
22 | SPZ | 850 | 0.85
23 | SPZ | 862 | 0.85
24 | SPZ | 875 | 0.85
25 | SPZ | 887 | 0.85
26 | SPZ | 900 | 0.9
27 | SPZ | 912 | 0.9
28 | SPZ | 925 | 0.9
29 | SPZ | 937 | 0.9
30 | SPZ | 950 | 0.9
31 | SPZ | 962 | 0.95
32 | SPZ | 987 | 0.95
33 | SPZ | 1000 | 0.95
34 | SPZ | 1012 | 0.95
35 | SPZ | 1024 | 0.95
36 | SPZ | 1037 | 0.95
37 | SPZ | 1047 | 1
38 | SPZ | 1060 | 1
39 | SPZ | 1077 | 1
40 | SPZ | 1087 | 1
41 | SPZ | 1112 | 1
42 | SPZ | 1120 | 1.05
43 | SPZ | 1137 | 1.05
44 | SPZ | 1162 | 1.05
45 | SPZ | 1180 | 1.05
46 | SPZ | 1187 | 0.8
47 | SPZ | 1202 | 0.8
48 | SPZ | 1212 | 0.8
49 | SPZ | 1237 | 0.85
50 | SPZ | 1250 | 0.85
51 | SPZ | 1262 | 0.85
52 | SPZ | 1287 | 0.85
53 | SPZ | 1312 | 0.85
54 | SPZ | 1320 | 0.9
55 | SPZ | 1337 | 0.9
56 | SPZ | 1347 | 0.9
57 | SPZ | 1362 | 0.9
58 | SPZ | 1387 | 0.9
59 | SPZ | 1400 | 0.95
60 | SPZ | 1412 | 0.95
61 | SPZ | 1437 | 0.95
62 | SPZ | 1462 | 0.95
63 | SPZ | 1487 | 0.95
64 | SPZ | 1500 | 1
65 | SPZ | 1512 | 1
66 | SPZ | 1537 | 1
67 | SPZ | 1562 | 1
68 | SPZ | 1587 | 1
69 | SPZ | 1600 | 1.05
70 | SPZ | 1612 | 1.05
71 | SPZ | 1637 | 1.05
72 | SPZ | 1662 | 0.8
73 | SPZ | 1687 | 0.8
74 | SPZ | 1700 | 0.8
75 | SPZ | 1737 | 0.8
76 | SPZ | 1762 | 0.85
77 | SPZ | 1787 | 0.85
78 | SPZ | 1800 | 0.85
79 | SPZ | 1812 | 0.85
80 | SPZ | 1837 | 0.9
81 | SPZ | 1862 | 0.9
82 | SPZ | 1887 | 0.9
83 | SPZ | 1900 | 0.9
84 | SPZ | 1937 | 0.9
85 | SPZ | 1987 | 0.95
86 | SPZ | 2000 | 0.95
87 | SPZ | 2037 | 0.95
88 | SPZ | 2120 | 0.95
89 | SPZ | 2137 | 0.95
90 | SPZ | 2150 | 1
91 | SPZ | 2187 | 1
92 | SPZ | 2240 | 1
93 | SPZ | 2287 | 1
94 | SPZ | 2360 | 1
95 | SPZ | 2500 | 1.05
96 | SPZ | 2540 | 1.05
97 | SPA | 570 | 1.05
98 | SPA | 590 | 1.05
99 | SPA | 620 | 1.05
100 | SPA | 640 | 1.05
101 | SPA | 670 | 1.05
102 | SPA | 690 | 1.05
103 | SPA | 720 | 1.05
104 | SPA | 732 | 1.05
105 | SPA | 782 | 1.05
106 | SPA | 800 | 1.05
107 | SPA | 850 | 1.05
108 | SPA | 875 | 1
109 | SPA | 882 | 1
110 | SPA | 900 | 1
111 | SPA | 932 | 1
112 | SPA | 950 | 1
113 | SPA | 967 | 1
114 | SPA | 982 | 1
115 | SPA | 1000 | 1
116 | SPA | 1032 | 1
117 | SPA | 1060 | 1
118 | SPA | 1082 | 1
119 | SPA | 1107 | 1
120 | SPA | 1132 | 1
121 | SPA | 1157 | 1
122 | SPA | 1180 | 1
123 | SPA | 1207 | 1
124 | SPA | 1232 | 1
125 | SPA | 1250 | 1
126 | SPA | 1282 | 1
127 | SPA | 1307 | 1
128 | SPA | 1320 | 1
129 | SPA | 1337 | 1
130 | SPA | 1382 | 1
131 | SPA | 1400 | 1
132 | SPA | 1432 | 1
133 | SPA | 1457 | 1
134 | SPA | 1482 | 1
135 | SPA | 1500 | 1
136 | SPA | 1532 | 1
137 | SPA | 1550 | 1
138 | SPA | 1557 | 1
139 | SPA | 1582 | 1
140 | SPA | 1600 | 1
141 | SPA | 1632 | 1
142 | SPA | 1657 | 1
143 | SPA | 1682 | 1
144 | SPA | 1700 | 1
145 | SPA | 1732 | 1
146 | SPA | 1757 | 1
147 | SPA | 1782 | 1
148 | SPA | 1800 | 1
149 | SPA | 1832 | 1
150 | SPA | 1850 | 1
151 | SPA | 1857 | 1
152 | SPA | 1882 | 1
153 | SPA | 1900 | 1
154 | SPA | 1932 | 1
155 | SPA | 1957 | 1
156 | SPA | 1982 | 1
157 | SPA | 2000 | 1
158 | SPA | 2020 | 1
159 | SPA | 2057 | 1
160 | SPA | 2082 | 1
161 | SPA | 2120 | 1
162 | SPA | 2132 | 1
163 | SPA | 2182 | 1
164 | SPA | 2207 | 1
165 | SPA | 2240 | 1
166 | SPA | 2282 | 1
167 | SPA | 2300 | 1
168 | SPA | 2332 | 1
169 | SPA | 2360 | 1
170 | SPA | 2382 | 1
171 | SPA | 2432 | 1
172 | SPA | 2500 | 1
173 | SPA | 2532 | 1
174 | SPA | 2582 | 1
175 | SPA | 2607 | 1
176 | SPA | 2632 | 1
177 | SPA | 2650 | 1
178 | SPA | 2682 | 1
179 | SPA | 2732 | 1
180 | SPA | 2782 | 1
181 | SPA | 2800 | 1
182 | SPA | 2832 | 1
183 | SPA | 2882 | 1
184 | SPA | 2900 | 1
185 | SPA | 2932 | 1
186 | SPA | 2982 | 1
187 | SPA | 3000 | 1
188 | SPA | 3030 | 1
189 | SPA | 3082 | 1
190 | SPA | 3150 | 1
191 | SPA | 3350 | 1
192 | SPA | 3550 | 1
193 | SPA | 3750 | 1
194 | SPA | 4000 | 1
195 | SPA | 4250 | 1
196 | SPB | 880 | 1
197 | SPB | 910 | 1
198 | SPB | 930 | 1
199 | SPB | 960 | 1
200 | SPB | 980 | 1
201 | SPB | 1000 | 1
202 | SPB | 1120 | 1
203 | SPB | 1250 | 1
204 | SPB | 1320 | 1
205 | SPB | 1400 | 1
206 | SPB | 1500 | 1
207 | SPB | 1600 | 1
208 | SPB | 1700 | 1
209 | SPB | 1800 | 1
210 | SPB | 1900 | 1
211 | SPB | 2000 | 1
212 | SPB | 2120 | 1
213 | SPB | 2150 | 1
214 | SPB | 2240 | 1
215 | SPB | 2285 | 1
216 | SPB | 2360 | 1
217 | SPB | 2500 | 1
218 | SPB | 2650 | 1
219 | SPB | 2800 | 1
220 | SPB | 2840 | 1
221 | SPB | 3000 | 1
222 | SPB | 3150 | 1
223 | SPB | 3350 | 1
224 | SPB | 3550 | 1
225 | SPB | 3650 | 1
226 | SPB | 3675 | 1
227 | SPB | 3750 | 1
228 | SPB | 3800 | 1
229 | SPB | 3825 | 1
230 | SPB | 4000 | 1
231 | SPB | 4060 | 1
232 | SPB | 4250 | 1
233 | SPB | 4310 | 1
234 | SPB | 4500 | 1
235 | SPB | 4750 | 1
236 | SPB | 5000 | 1
237 | SPB | 5300 | 1
238 | SPB | 5600 | 1